## Sheet1
[11 empty] | FALCON: 03-08-2021 |  |  |  | FALCON - 07.07.2021
PR FOR FIRE SEALING FOR MEP PENETRATION IN MCA | [14 empty] | 2021-06-02
Sr. No. | Item Description | MOC | Unit | Rate | Quantity per floor | Quantity from 31 floor to 62 floor | [7 empty] | Grand Total | Location/Area |  | Calculation Details
[6 empty] | Tower A |  | Tower B |  | Tower C |  | Tower D |  |  |  | Sealant required per sleeve | Sealant required per sleeve | Total Sealant required | wrap required per sleeve | Sealant cost per sleeve | Wrap cost per sleeve | Application cost per sleeve | Total Material cost per sleeve | Total cost material and labour
[6 empty] | Total floors | Total Quantity | Total floors | Total Quantity | Total floors | Total Quantity | Total floors | Total Quantity
Providing & installation fire proofing for MEP penetrations in Master Common Area:
a) | 50mm dia core X 32mm dia pipe X200mm depth | RCC Core and PVC | Nos. | 90.1769 | 18 | 32 | 576 | 32 | 576 | 32 | 576 | 32 | 576 | 2304 | Sub Mains | 0.19 | 0.1995 | 459.648 | 0 | 46.0845 | 0 | 44.0924 | 46.0845 | 90.1769 | 207767.6428
b) | 50mm dia core X 12mm dia pipe X100mm depth | RCC Core and FRLS | Nos. | 85.4308 | 2 | 32 | 64 | 32 | 64 | 32 | 64 | 32 | 64 | 256 | FAPA Cables | 0.18 | 0.189 | 48.384 | 0 | 43.659 | 0 | 41.7718 | 43.659 | 85.4308 | 21870.2782
c) | 80mm dia core X 50mm dia pipe X200mm depth | RCC Core and GI Pipe | Nos. | 142.3846 | 8 | 32 | 256 | 32 | 256 | 32 | 256 | 32 | 256 | 1024 | Fire Fighting | 0.3 | 0.315 | 322.56 | 0 | 72.765 | 0 | 69.6196 | 72.765 | 142.3846 | 145801.8546
d) | 80mm dia core X 65mm dia pipe X200mm depth | RCC Core and GI Pipe | Nos. | 80.6846 | 4 | 32 | 128 | 32 | 128 | 32 | 128 | 32 | 128 | 512 | Fire Fighting | 0.17 | 0.1785 | 91.392 | 0 | 41.2335 | 0 | 39.4511 | 41.2335 | 80.6846 | 41310.5255
e) | 50mm dia core X 20mm dia pipe X200mm depth | RCC Core and FRLS | Nos. | 75.9385 | 2 | 32 | 64 | 32 | 64 | 32 | 64 | 32 | 64 | 256 | Staircase speaker | 0.16 | 0.168 | 43.008 | 0 | 38.808 | 0 | 37.1305 | 38.808 | 75.9385 | 19440.2473
f) | 150mm dia core X 80mm dia pipe X200mm depth | RCC Core and FRLS | Nos. | 579.0308 | 1 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 128 | ELV Cables | 1.22 | 1.281 | 163.968 | 0 | 295.911 | 0 | 283.1198 | 295.911 | 579.0308 | 74115.9428
g) | 150mm dia core X 75mm dia pipe X200mm depth | RCC Core and PVC Pipe | Nos. | 1630.617 | 1 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 128 | MCA Drain | 2.14 | 2.247 | 287.616 | 0.06 | 519.057 | 614.94 | 496.62 | 1133.997 | 1630.617 | 208718.9737
h) | 75mm dia core X 50mm dia pipe X425mm depth | RCC Core and GI Pipe | Nos. | 113.9077 | 6 | 32 | 192 | 32 | 192 | 32 | 192 | 32 | 192 | 768 | Sprinkler entry into apartment | 0.24 | 0.252 | 193.536 | 0 | 58.212 | 0 | 55.6957 | 58.212 | 113.9077 | 87481.1128
I) | 50mm dia core X 12mm dia pipe X425mm depth | RCC Core and FRLS | Nos. | 85.4308 | 6 | 32 | 192 | 32 | 192 | 32 | 192 | 32 | 192 | 768 | Mobile Booster for Apartment | 0.18 | 0.189 | 145.152 | 0 | 43.659 | 0 | 41.7718 | 43.659 | 85.4308 | 65610.8346
j) | 100mm dia core X 80mm dia pipe X230mm depth | RCC Core and GI Pipe | Nos. | 128.1462 | 1 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 128 | Sprinkler Riser to zone control valve | 0.27 | 0.2835 | 36.288 | 0 | 65.4885 | 0 | 62.6577 | 65.4885 | 128.1462 | 16402.7086
k) | 100mm dia core X 80mm dia pipe X230mm depth | RCC Core and GI Pipe | Nos. | 128.1462 | 1 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 128 | Sprinkler Entry to MCA | 0.27 | 0.2835 | 36.288 | 0 | 65.4885 | 0 | 62.6577 | 65.4885 | 128.1462 | 16402.7086
L) | 75mm dia core X 32mm dia pipe X230mm depth | RCC Core and GI Pipe | Nos. | 166.1154 | 1 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 128 | Test drain , sprinkler header pipe entry to shaft | 0.35 | 0.3675 | 47.04 | 0 | 84.8925 | 0 | 81.2229 | 84.8925 | 166.1154 | 21262.7705
[14 empty] | 6528 |  |  |  | 1874.88 | [6 empty] | 926185.6
| Material | Product name | Packing | Cost / Packing | Quantity | Total
| Fire Sealant | Protecta FR Acrylic | 310 ml Cartridge | 231 | 1874.88 | 433097.28
| Application Charges |  | Per cartridge | 200 | 1874.88 | 374976 | [9 empty] | 1537.35
| Rockwool | Rockwool | 0.6 sq mt | 197 | 200 | 39400 | 21.0147
| Intumescent Wrap/ Strip | Protecta FR Pipe Wrap | 25 mt roll | 10249 | 10 | 102490
949963.28
| System | Drawings | Certification agency | Certificate | Drawing details
| System for GI Pipe | Attached In mail | UL-EU |  | Pg no. 118
| System for Cable | Attached In mail | UL-EU |  | Pg no. 114
| System for PVC pipes (75mm) | Attached In mail | UL-EU |  | Pg no. 142
| System for PVC conduits (32mm) | Attached In mail | UL-EU |  | Pg no. 148 / 211
NOTE: | GST & TRANSPORTATION EXTRA AT ACTUALS
PAYMENT TERMS 50% ON MATERIAL DELIVERY AND BALANCE ON COMPLETION
SCAFOLDING IF REQUIRED WILL BE CHARGED EXTRA AT ACTUALS
QUOTATION IS VALID FOR 30 DAYS
SEALANT REQUIRED PER FLOOR IS 14 NOS. AS PER THEOROTICAL CALUCALTION ON THE BOQ MEASUREMENTS.
ANY INCREASE IN THE QTY OF SEALANT REQUIRED PER FLOOR ON SITE AT THE TIME OF PRACTICAL APPLICATION WILL BE INTIMATED AND BE SUBJECTED TO ADDITIONAL BILLING.
SOLUTION DETAILS
For all PVC pipe penetrations, sealant will be applied at 25 mm depth both sides
Upto 32 mm dia PVC pipes, no wraps required
for PVC pipes with higher diameter, refer to the pipe wrap table for number of turns required
Metal pipes and Cable penetration, sealant will be applied at 15mm depth both sides

## Sheet2
| A1 | A2
| 314.2 | 176.7375
377.04 | 137.4625
15.0816 | 687.3125
0.15082 | 2.2171
15.0816 |  |  | 490.0095
|  |  | 512.1587 | 2049.5087
2539.5181
Note on P15: Author: Application Cost
Note on P16: Author: Sealant Cost